Advanced Protection Schemes for DFIG Based Wind Turbines during the Grid Faults
Alaa Eldin M. Abofard 1
1 Alexandria Higher Institute of Engineering & Technology (AIET), Alexandria, Egypt.
E-mail: alaaabofard@yahoo.com
Emad H. El-Zohri 2*, Heba A. Mahmoud 2**
2 Faculty of Industrial Education, 
Sohag University, Sohag, Egypt.
* E-mail: emad.elzohri@yahoo.com
** E-mail:  heba.ahmeden@yahoo.com
Hamdy A. Ziedan 3***
3 Faculty of Engineering, Assiut University, Assiut, Egypt.
*** E-mail: ziedan092@yahoo.com

Abstract—Negative impacts of the grid faults in the Doubly Fed Induction Generators (DFIGs) based wind turbines systems include the stator and rotor over currents, DC-link over voltage, electromagnetic torque oscillations, active and reactive power fluctuations at the grid connection point, potentially leading to destabilization of the power system network. For eliminating of the negative impacts, thus enhances the DFIGs based wind turbines performance. This paper proposes a comprehensive study about the performance analysis of a 1.5 MW DFIG-based wind turbine in order to stay connected to the grid under the symmetrical and asymmetrical grid faults. This study discusses and compares the simulations of two improved protection schemes to limit the negative impacts of the grid connected faults. The investigated protection schemes are simple in construction and cost efficient. The performance of the DFIG is highly improved during the grid faults. The simulation results confirm the effectiveness of these schemes. 
Keywords - wind Energy; wind turbines; DFIG; protection schemes.
I.  Introduction
Wind, as a well-known renewable energy resource, has stood out to be one of the most promising alternative sources of electrical power. It is environmentally friendly as means of dealing with the world energy shortage, and it is now considered as an actual alternative to the conventional and polluting energy sources such as oil, gas, and coal [1]. According to WWEA, more than 50 GW of capacity were added during the year 2014, bringing the total wind power capacity close to 370 GW [2]. The wind turbines installed up to now are mainly of the fixed speed type; this type of wind turbines has a number of drawbacks. They can only operate within a very narrow speed range above the synchronous speed, and consume reactive power. As a result of being directly connected to the grid. Wind speed variations are directly translated into voltage and power fluctuations at the grid connection point, potentially leading to destabilization of the power system network [3-5].While these turbines are practically obsolete, they are used at a number of older wind farms, and are not expected to be replaced by more modern wind turbines until they reach the end of their economic life, typically around 20 to 25 years from installation.  Most of the drawbacks that are mentioned are avoided when variable speed wind turbines are used. These turbines improve the dynamic behavior of the turbine and reduce the noise at low wind speeds. The power production of variable-speed turbines is higher than for fixed-speed turbines, and the energy they produce is of better quality, as they can rotate at the optimal rotational speed for each wind speed. Other advantages of variable-speed wind turbines are that they reduce mechanical stresses, and that they compensate for torque and power pulsations. Variable speed turbines are now prevailing, as their performance is superior and are considered likely to constitute a large portion of the generation mix for wind farms. Within variable speed wind generators, the most widely used across the for new installations in the last few years, and cost-effective are those based on a doubly fed induction generator (DFIG) as they use a power converter rated to a fraction of the total power. Therefore, the losses in the converter can be reduced and the cost of the converter becomes lower [6]. This has the capability to generate and consume active and reactive power in a controlled manner. The rotor converter allows independent control of the wind turbine active and reactive power. Wind turbines can operate both above and below the machine’s synchronous speed. Above the synchronous speed, the rotor converter injects active power to the grid, whereas below the synchronous speed power is consumed in the rotor from the grid.  This provides an operating speed range of around ±25–35% of the rated speed [4]. Another advantage of this type is that the mechanical drive train is largely decoupled from the electrical system via the back-to-back converter. This means that variations in the prime mover do not have a pronounced impact on the grid, resulting in reduced flicker levels, and power factor control for the overall system. However, wind turbines based on the DFIG are very sensitive to grid voltage disturbance for symmetrical and asymmetrical voltage dips as described in [7] and [8]. A sudden drop of the grid voltage symmetrical and asymmetrical occurred at the generator terminals. The DFIG stator currents dramatically increase beyond the rated values. Because of the magnetic coupling between stator and rotor, the stator fault currents are transmitted into the rotor causing uncontrollable excessive rotor over-currents. These currents can damage the power electronic devices of the converter. 

Also, the electromagnetic torque of the DFIG starts to oscillate with high amplitude causing mechanical stresses to the wind turbine system [9]. Initially, the solution implemented by the manufacturers to protect the converter was to short circuit the rotor windings with the so-called crowbar and disconnect the turbine from the grid. With this solution, they contribute to increase the dip as they stop generating electric power. For example, the European outage on November 4, 2006, caused the disconnection of 2800 MW of wind-origin power in Spain [10]. Thus these renewable generators will unlike conventional power plants not be able to support the voltage and the frequency of the grid during and immediately following the grid failure. This would cause major problems for the systems stability. It is therefore worldwide recognized that to enable large-scale application of wind energy without compromising system stability, the turbines should stay connected to the grid in case of a failure. They should similar to conventional power plants. Therefore, researchers are addressing the issue from several points of view. These points of view can be divided into two categories: modifying the DFIGs converters conventional control and extra hardware modification. The first is the means of designing more advanced control strategies for the rotor and grid side converters [11–19]. However, some of these algorithms have a number of drawbacks such as   too complicated to implement in industrial applications and depend strongly on the proper design of the control parameters or the estimation of certain parameters, which may have adverse effects on its robustness. However, these make the control systems complex or increase the issues with control coordination between normal and fault operation, the disadvantage of the variable-speed turbine is a more complex electrical system, the other is to extra hardware modification such as based on the conventional crowbar protection. Some improved crowbar solutions have been proposed to enhance the LVRT performance of the DFIG WT [20]–[25]. Although the crowbar circuit is short circuits the rotor terminals and isolates the RSC from the rotor that provides conservative protection to the RSC. But, at the same time changes the DFIG to a squirrel cage induction generator, which absorbs reactive power from the grid when reactive power support is required. As result, static and dynamic VAR compensators or STATCOMs are sometimes installed at the DFIGs terminals to provide reactive power during the grid faults , and dynamic voltage restorers [26, 27], flexible alternating current transmission systems (FACTSs) [28,29], and resistors [30 - 33]. However, these solutions increases complexity and cost of the wind turbines system, the most of the approaches show results for the symmetrical grid faults, whereas majority of the grid faults in the power system are asymmetrical, Considering these drawbacks, This paper presents two ways to Improved protection scheme for DFIG during symmetrical and asymmetrical voltage dips, The key idea is Improved extra hardware for DFIG. the two ways are: The first is Series Resistor Protection (scheme1) based on a series resistor (SR) is switched in series with the rotor winding, in normal operation, the switch is on and the resistor is bypassed; during fault conditions, the switch is off   throughout the period of the fault and the resistor is connected in series to the rotor winding.SR can share the rotor circuit voltage and hence   limits the rotor over current during the fault, and is an alternative to crowbar protection, Being controlled by a power electronic switch. The other is Crowbar and DC-chopper Protection (scheme2) contains two protection circuits a DC-chopper and crowbar. A crowbar is a set of resistors that are connected in parallel with the rotor winding. The crowbar firing is triggered by increasing the value of rotor current with the converter is blocked during the fault .thus the current continues to flow into the DC-link through the freewheeling diodes leading to a very fast voltage increase and Thus the DC-chopper is switched on for limit overvoltage .Different from conventional methods, is based on a simple concept, decrease cost and complexity of system, Useful under symmetrical and asymmetrical grid faults, Decrease rotor over current, DC-link over voltage and torque oscillations thus contribute to the system stability during the grid faults. The paper is organized as follows: in section 2, shows Effects of The Grid Faults in the DFIG Based wind Turbine   and in section 3 advanced protection schemes are presented and the DFIG behavior simulation under grid faults is analyzed.  Section 4 discusses the simulation results of DFIG system under fault and using two advanced protection schemes for DFIG during grid faults. Finally, concluding remarks on the use of such protecting device for DFIG application end the paper.
II. Effects of the Grid Faults on the DFIG Based Wind Turbine

A. DFIG based wind turbine Modeling

The block diagram of the grid connected wind energy conversion system is shown in Fig .1. The DFIG based wind turbine system consists of the wind turbine, drive train, induction generator, back-to-back PWM converters, and control system. It is connected to the grid through a transformer. The control system consists of two control levels: wind turbine control and DFIG control. The DFIG control level includes the rotor and grid side controllers. It controls the active and reactive power of the DFIG machine using the vector control technique [34]. 

B. Effects of  The symmetrical and asymmetrical grid faults

The magnetic flux of the machine is divided into two components. The first component corresponds to the “forced flux” that rotates at the synchronous speed. It is related to the stator voltage. The forced flux appears during the normal operation of the machine. The second component is called natural flux. It appears during voltage transients. Each component induces voltages in the rotor. The voltage 

induced by the forced flux is small. During gird faults, voltages are induced by the natural flux alone. The induced voltage amplitude is proportional to the depth of the grid voltage type and dip [7, 8]. 

If the depth of the dip is small and the voltage induced does not exceed the maximum voltage that the rotor converter can generate, the current remains controlled. In this case, as in the normal operation, the voltage at rotor terminals, for larger dips, the voltage induced exceeds the maximum available tension of the converter and the control of the current is lost transitorily. In this situation, there appear over currents that increase as the depth of the dip is bigger. This is transitory, only happens at the beginning (or end) of the dip, that is, when the grid voltages change abruptly. In asymmetrical dips a three-phase voltage system can be expressed as the sum of three components: positive, negative, and zero sequences. the positive sequence  creates a flux  and negative sequence  creates a flux  Each flux induces a voltage in the rotor, the nature of these voltages is different; not only do they have transitory components, such as those originated in symmetrical dips, but they also have permanent components that remain throughout the whole dip, Besides. Asymmetrical dips are more harmful to the generator than are symmetrical dips, since they induce higher voltages in the rotor. Those are much greater than those 
appearing under normal operation. To demonstrate the important difference between symmetrical and asymmetrical faults an extensive simulation study, using the MATLAB/Simulink, is conducted on a 9 MW (10 MVA) wind farm consisting of six 1.5MW DFIG-based wind turbines, Before the moment of grid faults occurrence, in order to simulate the most onerous Grid Faults conditions that can be imposed on the DFIGs, generators operate in super synchronous mode; the rotors speed are 1.2 pu and based on the optimal power-speed curve, the output active power of the wind farm is 9 MW. The output reactive power of the wind farm is zero. The fault located at the connection between 120/25 kV transformer and the 25 kV line, is simulated at t = 0.7s and cleared at t = 0.9 s at (see Figs.2). Simulated fault conditions are as follows:

i. The symmetrical fault in the 25 kV bus with p = 0.95pu Depth that is seem as A type sag in the generator terminals. Fault is occurred at t = 0.7 s and cleared at t = 0.9 s.

ii. The 2Φ asymmetrical fault in the 25 kV bus with that is seem as F type sag in the generator terminals. Fault is occurred at t = 0.7 s and cleared at t = 0.9 s.
C. Operation under the symmetrical fault

Figure 3 shows the system responses to a 0.95 p.u. grid voltage dip for 0.2 s. As it is noticed in Figure the grid voltage is decreased that indicates 0.95 pu grid voltage sag depth lead to increased considerably currents in the stator, since in the symmetrical fault the increase of the current this is only happens at the beginning (or end) of the dip As it is noticed in Figure which reach around 2.66 pu, For the most serious phase. Voltage dips that lead also to appear “natural flux” in the machine thus induces voltages in the rotor. In this situation, there appear over currents that increase at the beginning (or end) of the dip which reach around 2.5 pu. , For the most serious phase. That led also to rising DC-link voltage. The DC-capacitor is usually not able to reduce this effect considerably. The wind turbine shaft will experience oscillating torque the first peak of which reaching almost 0.7 pu leading to severe stressing of the turbine shaft, Fluctuations in both the active and reactive power.

D. Operation under the 2Φ asymmetrical fault

Figure 4 shows the system responses during asymmetrical fault conditions here, phase's b and c are shorted together leading to a voltage dip at the stator Terminals. As described in the previous section, induces a voltage in the rotor, the nature of these voltages is different; they also have permanent components that remain throughout the whole dip, As it is evident in the increase both the  stator  and rotor currents that remain throughout the whole dip, Since in the increase stator currents reach around 2.09pu. For the most serious phase, and increase the rotor currents reach around 1.91pu .for the most serious phase. Thus higher rotor currents lead also to rising DC-link voltage, the peak value of which reaching almost 1298 v and large electrical torque fluctuations occur, the peak value of which around 0.37 pu. Large fluctuations occur in both the active and reactive power.
III- Advanced protection schemes

In this section, presents Two of Advanced protection schemes for DFIG based wind turbine during symmetrical and asymmetrical voltage dips:

A. Series Resistor Protection Scheme

The protection scheme based on a series resistor (SR) is in a similar way to the series dynamic braking resistor [35], which has been used in the stator side of generators, is to be switched in series with the rotor winding as shown in Fig .5. SR can share the rotor circuit voltage and hence   limits the rotor over current during the fault.
Being controlled by a power electronic switch, in normal operation, the switch is on and the resistor is bypassed; during fault conditions, the switch is off   throughout the period of the fault and the resistor is connected wholly in series to the rotor winding, In other words, The inclusion of SR wholly within rotor circuit   throughout the period of fault. SR has several advantages through the topology, as SR has the distinct advantage of controlling the current magnitude directly. Moreover, with the SR, the high voltage will be shared by the resistance because of the series topology; therefore, the induced overvoltage may not lead to the loss of converter control. Hence, it not only controls the rotor overvoltage which could cause the rotor-side converter to lose control, but also limits the high rotor current. In addition, limiting the current reduces the charging current of the DC-link capacitor, which helps avoid DC-link overvoltage. Therefore, with the SR, the rotor-side converter does not need to be inhibited during the fault. Another advantage for the SR is based on a simple concept to dissipated induces voltages in the rotor appears during the fault. Where the resistance value that is inserted in the rotor circuit is 0.018 and its value is small, this is for all   fault conditions.
B. Crowbar and DC-chopper  Protection Scheme

The Protection scheme contains two protection circuits a DC-chopper and crowbar as shown in Fig.6. A crowbar is a set of resistors that are connected in parallel with the rotor winding. The crowbar firing is triggered by increasing the value of rotor current with the converter is blocked during the fault .thus the current continues to flow into the DC-link through the freewheeling diodes leading to a very fast voltage increase and thus the DC-chopper is switched on for limit overvoltage. In the past years, many curricula have been presented to use Crowbar Protection to protect the converter. However, show results for the symmetrical grid faults. But in this paper has been improved these circuits in order to 
benefit from resistors  to reduce rotor current and DC-link overvoltage with the converter is blocked during the symmetrical and asymmetrical grid faults. Where the specific values of resistors for each of the crowbar and DC-chopper are RCB = 10000Ω and RDCC = 11Ω. 
IV- Behavior of DFIG-Based Wind Turbine  under Series Resistor protection scheme during Grid Faults

A. Symmetrical Fault Condition

Figures 7 show the system response to a 0.95 p.u. voltage dip for 0.2 s with Protection. In the simulation with protection, the inclusion of series resistance in the rotor circuit led to dissipate induced voltages in the rotor appeared during the fault. Thus damping both increase stator and rotor currents, since in stator currents are decreased from 2.66 pu to 2.02pu, For the most serious phase. And rotor currents are decreased from 2.5 pu to 1.21 p, For the most serious phase, And thus reduced significantly for each of the DC-link voltage and electrical torque fluctuations.
B. Asymmetrical Fault Conditions
Figure 8 shows the system responses during asymmetrical fault conditions. For The phase b to c short-circuit, series resistance show their effectiveness in terms of dissipation induced voltage in the rotor so that the decreased of the stator currents from 2.09 pu to 1.04 pu, For the most serious phase. and rotor currents  are decreased from 1.91pu   to 1.104pu,For the most serious phase, And thus reduced significantly for each of the DC-link voltage and electrical torque fluctuations.
V- Behavior of DFIG-Based Wind Turbine  under Crowbar and a DC-chopper protection scheme during Grid Faults

A. Symmetrical Fault Condition

Figure 9 shows the system response at 0.95 p.u. voltage dip for 0.2 s with protection. The crowbar firing is triggered by the rotor currents which rise due to the first rotor current peak. The IGBTs are usually stopped by the protection but the current and thus the energy continue to flow into the DC-link through the freewheeling diodes leading to a very fast voltage increase and thus the DC-
chopper is switched on to limit overvoltage. The included parallel resistance in the rotor circuit and also connected resistance in parallel with DC-link, this leads to decrease of the stator currents from 2.66 pu   to 1.81pu, for the most serious phase. And rotor currents are decreased from 2.5 pu to 1.42 pu, For the most serious phase, And thus reduced significantly for each of the DC-link voltage and electrical torque fluctuations.
B. Asymmetrical Fault Condition

Figure 10.  Shows the system responses during asymmetrical fault condition, the phase b to c short-circuit; the crowbar protection and DC-chopper switching events are similar to the symmetrical fault condition. Lead to the decreased of the stator currents from 2.09pu   to 1.38p, for the most serious phase. And rotor currents are decreased from 1.91pu to 1.06 pu, For the most serious phase, And thus reduced significantly for each of the DC-link voltage and electrical torque fluctuations.
VI- Discussion

In the simulation model, the performance analysis of a 1.5 MW DFIG-based wind turbine under the symmetrical and asymmetrical grid faults. For eliminating of the negative impacts of the  grid faults in the system  It was used two  improved  protection schemes and comparing the simulations of two protection schemes, And through the simulation results that have been presented in previous sections can be seen that SR protection is more effective than Crowbar and DC-chopper Protection  in terms of damping  currents increase at the generator terminals which contributes to the stability of the system during the fault period, AS for the absorber for efforts induced in the rotor in the case of  use SR protection have  the series topology. Therefore, the induced overvoltage will be shared by the resistance. Thus dissipate within resistance which the reduced rotor currents and better than Crowbar and DC-chopper Protection. Both of the two strategies experience reactive power and electrical torque fluctuations during the fault. However, for crowbar protection, they are much larger.  It can be seen that with the RSC connected with the SR protection scheme, no reactive power is absorbed. However, for crowbar and dc chopper protection, the asynchronous machine absorbs reactive power. Therefore, in terms of grid voltage recovery, the SR protection has a significant advantage. Electrical torque ripple is larger with SR protection compared to crowbar protection. More importantly, the SR has a much smaller impact than the Crowbar and DC-chopper protection.

VII- conclusions

The Eliminating of the negative impacts of the grid faults in the  DFIG based wind turbines systems  and enhances the DFIGs based wind turbines performance has been investigated considering two protection schemes by using the DFIG to stabilize. A grid fault affects both the mechanical and electrical components of the wind turbine. Therefore, it is imperative to protect the generator to avoid damage of its power converters during a grid fault. Though the two protection schemes investigated in this study are both effective in protecting the DFIG, it can be concluded that the scheme 1 is superior to scheme 2 considering the issues of low component cost and better performance. The purpose of an SR is to avoid the frequent use of crowbar short-circuit, to maximize the operation time of the RSC, and to reduce the voltage induced in the rotor during protection operation.

References
[1]
J. Yang, "Fault analysis and protection for wind power generation systems," University of Glasgow, 2011.

[2]
http://wwindea.org
[3]
M. Rodriquez, G. Abad, I. Sarasola, and A. Gilabert, "Crowbar control algorithms for doubly fed induction generator during voltage dips," in Power Electronics and Applications, 2005 European Conference on, 2005, pp. 10 pp.-P. 10.

[4]
A. E. M. Operator, "WIND TURBINE PLANT CAPABILITIES REPORT 2013 Wind Integration Studies", ed, 2013.

[5]
J. Morren and S. W. De Haan, "Ridethrough of wind turbines with doubly-fed induction generator during a voltage dip," Energy conversion, ieee transactions on, vol. 20, pp. 435-441, 2005.
[6]
Z. Peng and H. Yikang, "Control strategy of an active crowbar for DFIG based wind turbine under grid voltage dips," in Electrical Machines and Systems, 2007.ICEMS. International Conference on, 2007, pp. 259-264.

[7]
J. Lopez, P. Sanchis, X. Roboam, and L. Marroyo, "Dynamic behavior of the doubly fed induction generator during three-phase voltage dips," Energy Conversion, IEEE Transactions on, vol. 22, pp. 709-717, 2007.

[8]
J. Lopez, E. Gubia, P. Sanchis, X. Roboam, and L. Marroyo, "Wind turbines based on doubly fed induction generator under asymmetrical voltage dips," Energy Conversion, IEEE Transactions on, vol. 23, pp. 321-330, 2008.

[9]
Z. Peng, H. Yikang, “Control Strategy of an Active Crowbar for DFIG Based Wind turbine under Grid Voltage Dips”, Electrical Machines and Systems, ICEMS 2007, pp. 259-264, 2007.

[10]
REE, Unfallo en la red de altatensi´on de Alemaniaprovocacortes de suministro envariospa´ıses, Nov. 5, 2006. [Online]. Available: http://www.ree.es/apps/ver_not.asp.

 [11]
D. Xiang, L. Ran, P. J. Tavner, and S. Yang, “Control of a doubly-fedinduction generator in a wind turbine during grid fault ride-through,”IEEE Trans. Energy Convers., vol. 21, no. 3, pp. 652–662, Sep. 2006.

[12]
M. Rathi and N. Mohan, “A novel robust low voltage and fault ridethrough for wind turbine application operating in weak grids,” in Proc.IEEE Industrial Electronics Society Conf., Nov. 2005, pp. 6–10.

[13]
A. Hansen and G. Michalke, “Fault ride-through capability of DFIGwind turbines,” Renew. Energy, vol. 32, no. 9, pp. 1594–1610, Jul.2007..

[14]
J. Lopez, P. Sanchis, X. Roboam, and L. Marroyo, “Dynamic behaviorof the doubly fed induction generator during three-phase voltage dips,”IEEE Trans. Energy Convers., vol. 22, no. 3, pp. 709–717, Sep. 2007

 [15] L. Xu and P. Cartwright, “Direct active and reactive power control of DFIG for wind energy generation,” IEEE Trans. Energy Convers., vol.21, no. 3, pp. 750–758, Sep. 2007

[16]
M. Rahimi and M. Parniani, “Transient performance improvement ofwind turbines with doubly fed induction generators using nonlinear control strategy,” IEEE Trans. Energy Convers., vol. 25, no. 2, pp. 514–525, Jun. 2010.

[17]
F. K. A. Lima, A. Luna, P. Rodriguez, E. H. Watanabe, and F. Blaabjerg,“Rotor voltage dynamics in the doubly fed induction generator during grid faults,” IEEE Trans. Power Electron., vol. 25, no. 1, pp. 118–130, Jan. 2010.

[18]
J. Liang, W. Qiao, and R. G. Harley, “Feed-forward transient currentcontrol for low-voltage ride-through enhancement of DFIG wind turbines,”IEEE Trans. Energy Convers., vol. 25, no. 3, pp. 836–843, Sep.2010.

[19]
J. Yao, H. Li, Y. Liao, and Z. Chen, “An improved control strategy oflimiting the DC-link voltage fluctuation for a doubly fed induction windgenerator,” IEEE Trans. Power Electron., vol. 23, no. 3, pp. 1205–1213,May 2008.

[20]
A. H. Kasem, E. F. EI-Saadany, H. H. EI-Tamaly, and M. A. A.Wahab,“An improved fault ride-through strategy for doubly fed induction generator-based wind turbines,” IET Renew. Power Gen., vol. 2, no. 4, pp. 201–214, Dec. 2008.

[21]
S. Foster, L. Xu, and B. Fox, “Coordinated reactive power control forfacilitating fault ride through of doubly fed induction generator- andfixed speed induction generator-based wind farms,” IET Renew. Power Gen., vol. 4, no. 2, pp. 128–138, Mar. 2008.

[22]
L. Peng, B. Francois, and Y. Li, “Improved crowbar control strategy ofDFIG based wind turbines for grid fault ride-through,” in Proc. IEEE24th Annu. Applied Power Electronics Conf. Expo., Washington, DC, Feb. 2009, pp. 1932–1938.

[23]
M. B. C. Salles, J. R. Cardoso, A. P. Grilo, C. Rahmann, and K.Hameyer, “Control strategies of doubly fed induction generators tosupport grid voltage,” in Proc. IEEE Int. Electric Machines and Drives Conf., May 2009, pp. 1551–1556.

[24]
J. López, E. Gubía, E. Olea, J. Ruiz, and L. Marroyo, “Ride throughof wind turbines with doubly fed induction generator under symmetricalvoltage dips,” IEEE Trans. Ind. Electron., vol. 56, no. 10, pp. 4246–4254, Oct. 2009.

[25]
L. G. Meegahapola, T. Littler, and D. Flynn, “Decoupled-DFIG faultride-through strategy for enhanced stability performance during gridfaults,” IEEE Trans. Sustain. Energy, vol. 1, no. 3, pp. 152–162, Oct. 2010.

[26]
Christian Wessels, Fabian Gebhardt, and Friedrich Willhelm Fuchs,"Fault ride-through of a DFIG wind turbine using a dynamic voltagerestorer during symmetrical and asymmetrical grid faults," IEEE Trans. Power Systems, vol. 26, no. 3, pp. 807-815, Mar. 2011.

[27]
Patrick S. Flannery, and GiriVenkataramanan, "A fault tolerant doubly fed induction generator wind turbine using a parallel gridside rectifier and series grid side converter," IEEE Trans. Power Electronics, vol. 23, no. 3, pp. 1126-1135, May. 2008.

[28]
K. E. Okedu, S. M. Muyeen, Rion Takahashi, and J. Tamura, "Participation of facts in stabilizing DFIG with crowbar during gridfault based on grid codes," in 2011 IEEE conference and exhibition, Dubai, pp. 365-368.

[29]
Zhou Linyuan, Liu Jinjun, and Liu Fangcheng, "Low voltage ride-through of wind farms using STATCOM combined with series dynamic breaking resistor," in 2010 2nd IEEE Int. Symp. Power Electronics for Distributed Generation Systems, pp. 841-845.

[30]
Andreas Dittrich, and Alexander Stoev, " Comparison of faultride-through strategy for wind turbines with DFIM generators," in2005 European Conf. Power Electronics and Application.

[31]
J. H. Zhang, X. Y. Chen, Bing Wang, Ping Wang, and Hao-MingLiu, "Three-phase short circuit analysis of DFIG-based wind generation and the crowbar biggest resistance setting," in 2009 IEEE Conf. SUPERGN.

[32]
Johan Morren, and Sjoerd W. H. de Haan, "Short-circuit current ofwind turbines with doubly fed induction generator," IEEE Trans. Energy Conversion, vol. 22, no. 1, pp. 174-180, May. 2007.

[33]
W. J. Chen, David Atkinson, Hamza Chaal, and MilutinJovanovic,"Experimental and simulation comparison for timer action crow barof doubly-fed induction generator," in 2011 IEEE Asia-Pacific Power and Energy Engineering Conf.

[34]
N. Ganesh and P. U. Rani, "Fault-Ride Through of a DFIG Wind Turbine using a Dynamic Voltage Restorer during Symmetrical and Asymmetrical Grid Faults".

[35]
C. a. a. Gavrilut__a and S. Sp_ataru, "DFIG Fault Ride Through Control," Student master thesis project Department of energy technology, Aalborg University, May 30, 2011.
